## bus
| name | vn_kv | type | zone | in_service
0 | Terrasa | 110 | b |  | TRUE
1 | Manresa | 110 | b |  | TRUE
2 | Tarrega | 110 | b |  | TRUE
3 | Montblanc | 110 | b |  | TRUE
4 | Vandellos | 110 | b |  | TRUE
5 | Lleida | 110 | b |  | TRUE
6 | Igualada | 110 | b |  | TRUE
7 | El Perellos | 110 | b |  | TRUE
8 | Agramunt | 110 | b |  | TRUE
9 | Valls | 110 | b |  | TRUE
10 | Falset | 110 | b |  | TRUE
11 | Conesa | 110 | b |  | TRUE
12 | Manresa_LV | 20 | b |  | TRUE
13 | Tarrega_LV | 20 | b |  | TRUE
14 | Montblanc_LV | 20 | b |  | TRUE
15 | Lleida_LV | 20 | b |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 |  | 5 | 90 | 18.27 | 0 | 0 |  | 1 | TRUE | wye
1 |  | 2 | 180 | 36.54 | 0 | 0 |  | 1 | TRUE | wye
2 |  | 1 | 90 | 18.27 | 0 | 0 |  | 1 | TRUE | wye
3 |  | 3 | 90 | 18.27 | 0 | 0 |  | 1 | TRUE | wye

## sgen
| name | bus | p_mw | q_mvar | sn_mva | scaling | in_service | type | current_source
0 |  | 5 | 30 | 10 |  | 1 | TRUE | wye | TRUE
1 |  | 5 | 100 | 20 |  | 1 | TRUE | wye | TRUE

## gen
| name | bus | p_mw | vm_pu | sn_mva | min_q_mvar | max_q_mvar | scaling | slack | in_service | slack_weight | type | controllable
0 |  | 4 | 190 | 1 |  |  |  | 1 | FALSE | TRUE | 0 |  | FALSE

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | Tarrega-Lleida |  | 2 | 5 | 44 | 0.062 | 0.39301 | 9.193 | 0 | 0.88898 | 1 | 1 |  | TRUE
1 | Tarrega-Igualada |  | 2 | 6 | 40 | 0.062 | 0.39301 | 9.193 | 0 | 0.88898 | 1 | 1 |  | TRUE
2 | Tarrega-Manresa |  | 2 | 1 | 58 | 0.031 | 0.17161 | 21.1613 | 0 | 1.778 | 1 | 1 |  | TRUE
3 | Manresa-Terrasa |  | 1 | 0 | 23 | 0.031 | 0.17161 | 21.1613 | 0 | 1.778 | 1 | 1 |  | TRUE
4 | Tarrega-Montblanc |  | 2 | 3 | 30 | 0.031 | 0.17161 | 21.1613 | 0 | 1.778 | 1 | 1 |  | TRUE
5 | Montblanc-Vandellos |  | 3 | 4 | 52 | 0.031 | 0.17161 | 21.1613 | 0 | 1.778 | 1 | 1 |  | TRUE
6 | Igualada-Terrassa |  | 6 | 0 | 33 | 0.062 | 0.17161 | 21.1613 | 0 | 1.778 | 1 | 1 |  | TRUE
7 | Vandellos-Lleida |  | 4 | 5 | 90 | 0.031 | 0.39301 | 9.193 | 0 | 0.88898 | 1 | 1 |  | TRUE
8 | Montblanc-Terrassa |  | 3 | 0 | 80 | 0.031 | 0.39301 | 9.193 | 0 | 0.88898 | 1 | 1 |  | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | Trafo_Manresa |  | 1 | 12 | 84 | 110 | 20 | 10 | 0.32 | 22 | 0.04 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE
1 | Trafo_Tarrega |  | 2 | 13 | 132 | 110 | 20 | 10 | 0.25 | 60 | 0.06 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE
2 | Trafo_Montblanc |  | 3 | 14 | 84 | 110 | 20 | 10 | 0.32 | 22 | 0.04 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE
3 | Trafo_Lleida |  | 5 | 15 | 84 | 110 | 20 | 10 | 0.32 | 22 | 0.04 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2.0179 | 41.5668
1 | 1.8169 | 41.724
2 | 1.1395 | 41.6469
3 | 1.1618 | 41.3748
4 | 0.87562 | 40.9562
5 | 0.61613 | 41.6154
6 | 1.6191 | 41.5807
7 | 0.71262 | 40.8754
8 | 1.0866 | 41.7915
9 | 1.2476 | 41.2843
10 | 0.82771 | 41.1439
11 | 1.2716 | 41.5022
12 | 1.8121 | 41.7152
13 | 1.1518 | 41.6416
14 | 1.154 | 41.3747
15 | 0.61427 | 41.6126

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1 | 0 | -96.6154 | -58.0768
1 | 0.96968 | -1.4515 | 50 | 10.15
2 | 0.91569 | -2.9299 | 120 | 24.36
3 | 0.93435 | 0.79719 | 50 | 10.15
4 | 1 | 8.8784 | -190 | -30.8618
5 | 0.8841 | -7.8422 | 50 | 10.15
6 | 0.91652 | -2.9381 | 0 | 0
7 |  |  | 0 | 0
8 |  |  | 0 | 0
9 |  |  | 0 | 0
10 |  |  | 0 | 0
11 |  |  | 0 | 0
12 | 0.96966 | -1.4523 | 0 | 0
13 | 0.91567 | -2.9312 | 0 | 0
14 | 0.93434 | 0.79647 | 0 | 0
15 | 0.88409 | -7.8429 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 50.7652 | 13.6658 | -50.0172 | -10.1699 | 0.748 | 3.496 | 0.30134 | 0.30301 | 0.30301 | 0.91569 | -2.9299 | 0.8841 | -7.8422 | 34.0853
1 | 8.41e-05 | -1.1726 | 2.6015e-14 | -1.3352e-15 | 8.41e-05 | -1.1726 | 0.0067212 | 1.4918e-16 | 0.0067212 | 0.91569 | -2.9299 | 0.91652 | -2.9381 | 0.75605
2 | -43.7225 | -45.897 | 45.0844 | 45.5172 | 1.3619 | -0.37979 | 0.36334 | 0.34677 | 0.36334 | 0.91569 | -2.9299 | 0.96968 | -1.4515 | 20.4358
3 | -95.1051 | -55.6911 | 96.6154 | 58.0768 | 1.5104 | 2.3857 | 0.59655 | 0.59167 | 0.59655 | 0.96968 | -1.4515 | 1 | 0 | 33.5523
4 | -127.0931 | 9.0004 | 130.0727 | -2.8181 | 2.9796 | 6.1823 | 0.73031 | 0.73085 | 0.73085 | 0.91569 | -2.9299 | 0.93435 | 0.79719 | 41.1058
5 | -180.092 | -7.3541 | 190 | 30.8618 | 9.908 | 23.5077 | 1.0125 | 1.0103 | 1.0125 | 0.93435 | 0.79719 | 1 | 8.8784 | 56.947

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 0.020685 | 0.023879 | 4.0938e-15 | -1.1038e-13 | 0.020685 | 0.023879 | 0.000171 | 3.2883e-15 | 0.96968 | -1.4515 | 0.96966 | -1.4523 | 0.038787
1 | 0.050307 | 0.043348 | -4.1488e-15 | -2.0826e-13 | 0.050307 | 0.043348 | 0.00038064 | 6.5669e-15 | 0.91569 | -2.9299 | 0.91567 | -2.9312 | 0.05494
2 | 0.019206 | 0.022171 | -8.1148e-15 | 1.0612e-13 | 0.019206 | 0.022171 | 0.00016477 | 3.2883e-15 | 0.93435 | 0.79719 | 0.93434 | 0.79647 | 0.037373
3 | 0.017196 | 0.019851 | -3.6069e-14 | 1.0643e-13 | 0.017196 | 0.019851 | 0.00015591 | 3.6692e-15 | 0.8841 | -7.8422 | 0.88409 | -7.8429 | 0.035364

## res_ext_grid
| p_mw | q_mvar
0 | 96.6154 | 58.0768

## res_load
| p_mw | q_mvar
0 | 50 | 10.15
1 | 120 | 24.36
2 | 50 | 10.15
3 | 50 | 10.15

## res_gen
| p_mw | q_mvar | va_degree | vm_pu
0 | 190 | 30.8618 | 8.8784 | 1

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | gen | name | object
16 | gen | bus | uint32
17 | gen | p_mw | float64
18 | gen | vm_pu | int64
19 | gen | sn_mva | float64
20 | gen | min_q_mvar | float64
21 | gen | max_q_mvar | float64
22 | gen | scaling | float64
23 | gen | slack | bool
24 | gen | in_service | bool
25 | gen | slack_weight | float64
26 | gen | type | object
27 | gen | controllable | bool
28 | ext_grid | name | object
29 | ext_grid | bus | uint32
30 | ext_grid | vm_pu | float64
31 | ext_grid | va_degree | float64
32 | ext_grid | slack_weight | float64
33 | ext_grid | in_service | bool
34 | line | name | object
35 | line | std_type | object
36 | line | from_bus | uint32
37 | line | to_bus | uint32
38 | line | length_km | float64
39 | line | r_ohm_per_km | float64
40 | line | x_ohm_per_km | float64
41 | line | c_nf_per_km | float64
42 | line | g_us_per_km | float64
43 | line | max_i_ka | float64
44 | line | df | float64
45 | line | parallel | uint32
46 | line | type | object
47 | line | in_service | bool
48 | trafo | name | object
49 | trafo | std_type | object
50 | trafo | hv_bus | uint32
51 | trafo | lv_bus | uint32
52 | trafo | sn_mva | float64
53 | trafo | vn_hv_kv | float64
54 | trafo | vn_lv_kv | float64
55 | trafo | vk_percent | float64
56 | trafo | vkr_percent | float64
57 | trafo | pfe_kw | float64
58 | trafo | i0_percent | float64
59 | trafo | shift_degree | float64
60 | trafo | tap_side | object
61 | trafo | tap_neutral | float64
62 | trafo | tap_min | float64
63 | trafo | tap_max | float64
64 | trafo | tap_step_percent | float64
65 | trafo | tap_step_degree | float64
66 | trafo | tap_pos | float64
67 | trafo | tap_phase_shifter | bool
68 | trafo | parallel | uint32
69 | trafo | df | float64
70 | trafo | in_service | bool
71 | bus_geodata | x | float64
72 | bus_geodata | y | float64
73 | bus_geodata | coords | object
74 | res_bus | vm_pu | float64
75 | res_bus | va_degree | float64
76 | res_bus | p_mw | float64
77 | res_bus | q_mvar | float64
78 | res_line | p_from_mw | float64
79 | res_line | q_from_mvar | float64
80 | res_line | p_to_mw | float64
81 | res_line | q_to_mvar | float64
82 | res_line | pl_mw | float64
83 | res_line | ql_mvar | float64
84 | res_line | i_from_ka | float64
85 | res_line | i_to_ka | float64
86 | res_line | i_ka | float64
87 | res_line | vm_from_pu | float64
88 | res_line | va_from_degree | float64
89 | res_line | vm_to_pu | float64
90 | res_line | va_to_degree | float64
91 | res_line | loading_percent | float64
92 | res_trafo | p_hv_mw | float64
93 | res_trafo | q_hv_mvar | float64
94 | res_trafo | p_lv_mw | float64
95 | res_trafo | q_lv_mvar | float64
96 | res_trafo | pl_mw | float64
97 | res_trafo | ql_mvar | float64
98 | res_trafo | i_hv_ka | float64
99 | res_trafo | i_lv_ka | float64
100 | res_trafo | vm_hv_pu | float64
101 | res_trafo | va_hv_degree | float64
102 | res_trafo | vm_lv_pu | float64
103 | res_trafo | va_lv_degree | float64
104 | res_trafo | loading_percent | float64
105 | res_ext_grid | p_mw | float64
106 | res_ext_grid | q_mvar | float64
107 | res_load | p_mw | float64
108 | res_load | q_mvar | float64
109 | res_gen | p_mw | float64
110 | res_gen | q_mvar | float64
111 | res_gen | va_degree | float64
112 | res_gen | vm_pu | float64

## parameters
| version | format_version | converged | OPF_converged | name
0 | 2.14.10 | 2.14.0 | TRUE | FALSE